## CFM
TEST CERTIFICATE
CLIENT |  | : | PREMIUM SERUMS AND VACCINES PVT.LTD.
S.NO 354-1 ,354-2A/1 AT & POST-NARAYANGAON
TAL.JUNNAR. DIST PUNE- 410504
TEST CARRIED OUT BY |  | : | Mr.SHUBHAM NIRGUDE
TEST WITNESSED BY |  | : | Mr.AMAN PATHAN
TEST |  | : | CFM MEASUREMENT & ACPH TEST
VALIDATION DATE |  | : | 20/07/2023
TEST TAKEN |  | : | AT REST
AHU NO |  | : | AHU B 01
ROOM NAME & NO. |  | : | PRODUCTION OFFICE (14)
INSTRUMENT USED |  |  | CALIBRATION DATE |  |  | CALIBRATION DUE DATE
AIR CAPTURE HOOD |  |  | 2023-02-19 |  |  | 2024-02-18
MODEL NO.: 8380
MAKE : TSI ACCUBALANCE
SR. NO. : T83801931003
Sr. No. | Room Name & No. | Filter Code |  | Actual CFM | Total CFM |  | Room Vol. (Ft3) | ACPH
1 | PRODUCTION OFFICE (14) | AHU-B01-14-SH-07 |  | 302 | 678 |  | 1513.2 | 26.88
|  | AHU-B01-14-SH-08 |  | 376
ACCEPTANCE CRITERIA : AS PER ISO 14644-3:2019 ( E ) AIR CHANGES SHOULD NOT BE LESS THAN 20 ACPH
REFERANCE:-AS PER PROTOCOL No.: PSV/PRO/001
TEST CARRIED OUT BY |  |  | TEST WITNESSED BY |  |  | TEST REVIEWED BY
For, Micron HVAC Pvt. Ltd. |  |  | For,Premium Serums and Vaccines Pvt. Ltd.

## PAO
TEST CERTIFICATE
CLIENT |  | : | PREMIUM SERUMS AND VACCINES PVT.LTD.
S.NO 354-1 ,354-2A/1 AT & POST-NARAYANGAON
TAL.JUNNAR. DIST PUNE- 410504
TEST CARRIED OUT BY |  | : | Mr. SHANKAR PATIL
TEST WITNESSED BY |  | : | Mr. SHUBHAM BADHE
TEST |  | : | HEPA FILTER INTEGRITY TEST
VALIDATION DATE |  | : | 2022-03-16
TEST TAKEN |  | : | AT REST
AHU NO |  | : | AHU B 01
ROOM NAME & NO. |  | : | PACKING MATERIAL TESTING (45)
INSTRUMENT USED |  |  | CALIBRATION DATE |  |  |  | CALIBRATION DUE DATE
AEROSOL PHOTOMETER |  |  | 2021-10-02 |  |  |  | 2022-10-01
MODEL NO. :ATI 2i
SR / ID NO. :37504
PRESSURE GAUGE |  |  | 2026-02-08 |  |  |  | 2027-02-07
MODEL NO. :NIL
SR / ID NO. :MHPL/PG/1180
Room Name & No. | Filter No. |  | Upstream Conc. 20 To 80 µgm/lit (Before) | Upstream Conc. | Leakage (%) | Upstream Conc. 20 To 80 µgm/lit (After) | Upstream Conc. 85% To 115% (After÷Before×100) | PAO Test Result | Remarks
PACKING MATERIAL TESTING (45) | AHU-B01-45-SH-50 |  | 12 | 100% | 0% | 13 | 108.3333 | PASS | CLEARS PAO TEST
| AHU-B01-45-SH-51 |  | 14 | 100% | 0.001% | 13 | 92.8571 | PASS | CLEARS PAO TEST
ACCEPTANCE CRITERIA : AS PER ISO 14644-3:2019 ( E ) LEAKAGE NMT 0.01%
REFERANCE:-AS PER PROTOCOL No.PSV/PRO/001
TEST CARRIED OUT BY |  |  | TEST WITNESSED BY |  |  |  | TEST REVIEWED BY
For,Micron HVAC Pvt.Ltd. |  |  | For,Premium Serums and Vaccines Pvt. Ltd.

## PC REST
TEST CERTIFICATE
CLIENT |  | : | PREMIUM SERUMS AND VACCINES PVT.LTD.
S.NO 354-1 ,354-2A/1 AT & POST-NARAYANGAON
TAL.JUNNAR. DIST PUNE- 410504
TEST CARRIED OUT BY |  | : | Mr.ROSHAN BOLKE
TEST WITNESSED BY |  | : | M. GAUTAM NIKODI
TEST |  | : | NON-VIABLE PARTICLE COUNT TEST
VALIDATION DATE |  | : | 2022-03-16
TEST TAKEN |  | : | AT REST/IN OPERATION
AHU NO |  | : | AHU B 01
ROOM NAME & NO. |  | : | WASHING ROOM (51)
Instrument Details
Instrument Used: |  | Lasair_III Particle Counter
Sr. No. |  | 168867 |  |  | Make |  | PMS
Flow Rate |  | 100 LPM OR 28.3 LPM |  |  | Model No. |  | LasairIII_5100 OR LasairIII_310C
Sampling Volume |  | 0.1000 m3/min OR 0.0283 m3/min |  |  | Sampling Time |  | 1 Min UP TO 30 Min
Calibration Date |  | 22/05/2025 |  |  | Calibration Due on |  | 2026-05-22
Sr. No. | Room Name & No. | Location |  | No. of Particles in m3 |  | Remarks
|  |  |  | 0.5µ | 5.0µ
1 | WASHING ROOM (51) | L1 |  |  |  | Passes Class ISO 8 In At Rest Condition
L2
L3
L4
L5
REFERANCE:-AS PER PROTOCOL No.PSV/PRO/001
ACCEPTANCE CRITERIA AS PER ISO-14644-2:2015 (E ) or EU GMP
Maximum Permitted number of particles/m3 equal to or less than
No. | CLASS |  | 0.5µ |  | 5.0µ
1 | ISO-8 |  | 3520000 |  | 29300
TEST CARRIED OUT BY |  |  | TEST WITNESSED BY |  |  | TEST REVIEWED BY
For,Micron HVAC Pvt.Ltd. |  |  | For,Premium Serums and Vaccines Pvt. Ltd.

## RC
RECOVERY TEST
CLIENT |  | : | PREMIUM SERUMS AND VACCINES PVT.LTD.
S.NO 354-1 ,354-2A/1 AT & POST-NARAYANGAON
TAL.JUNNAR. DIST PUNE- 410504
TEST CARRIED OUT BY |  | : | Mr.HARSHVARDHAN PATIL
TEST WITNESSED BY |  | : | Mr.GAUTAM NAIKODI
TEST CARRIED OUT |  | : | RECOVERY TEST
VALIDATION DATE |  | : | 29/10/2025
AHU NO. |  | : | AHU F 12
Instrument Details
Instrument Used |  | LASAIR_III Particle Counter
Sr. No. |  | 72573 |  |  | Make |  | PMS
Flow Rate |  | 28.3 LPM |  |  | Model No. |  | 310C
Sampling Volume |  | 0.0283 m3 /m |  |  | Sampling Time |  | 01 min
Calibration Date |  | 08/10/2025 |  |  | Calibration Due on |  | 08/10/2026
Room Name & No. |  | AHU Condition | Time of Reading |  | No of Particles in m3 |  | Remarks
|  |  | START | END | 0.5µm | 5.0µm
STERIITY ROOM (FS 103) |  | Initial | 10:40 | 10:41 | 4343 | 0 | RECOVERY PERIOD IS 03 MIN.
|  | Generation | 10:46 | 10:47 | 515570 | 16910
|  | Recovery Period | 10:47 | 10:48 | 377947 | 3567
|  |  | 10:48 | 10:49 | 161210 | 1166
|  |  | 10:49 | 10:50 | 53267 | 212
|  |  | 10:50 | 10:51 | 6111 | 71
|  |  | 10:51 | 10:52 | 2508 | 0
A] Time at which Specified Class AHU Condition is ON : | [6 empty] | 10:47 | HH:MM:SS
B] Time at which Specified Class Condition is Achieved : | [6 empty] | 10:50 | HH:MM:SS
|  | Recovery Period = [B-A] : |  |  |  |  | 0:03 | H:MM:SS
Refrance:-AS PER PROTOCOL No.PSV/PRO/001
ACCEPTANCE CRITERIA:- NMT 15 Min AS PER ISPE & ISO-14644-3:2019 (E)
Maximum Permitted number of particles/mt3 equal to or less than
No. | CLASS |  | 0.5µm |  |  |  | 5.0µm
1 | ISO 6 |  | 35200 |  |  |  | 293
TEST CARRIED OUT BY, |  |  | TEST WITNESSED BY |  |  | TEST REVIEWED BY
For Micron HVAC Pvt.Ltd.Pune |  |  | For,Premium Serums and Vaccines Pvt. Ltd.

## Velocity
TEST CERTIFICATE
CLIENT |  | : | PREMIUM SERUMS AND VACCINES PVT.LTD.
S.NO 354-1 ,354-2A/1 AT & POST-NARAYANGAON
TAL.JUNNAR. DIST PUNE- 410504
TEST CARRIED OUT BY |  | : | Mr.PRASHANT UDGIRE
TEST WITNESSED BY |  | : | Mr. VIKAS BHOR
TEST CARRIED OUT |  | : | AIR VELOCITY TEST
VALIDATION DATE |  | : | 29/10/2025
AREA NAME |  | : | FFS
EQUIPMENT USED |  |  | CALIBRATION DATE |  |  | CALIBRATION DUE DATE
Digital Vane Probe Anemometer |  |  | 03/10/2025 |  |  | 02/10/2026
Model No. : AVM-04
Sr.No. : 230205234
Sr. No. | Equipment Name & ID. |  | Filter No. | Air Velocity Reading m/s / FPM |  |  |  |  | Average Air Velocity ( m/s) /FPM
|  |  |  | 1 | 2 | 3 | 4 | 5
1 | Laminar Air Flow (PSV/FF/PR/LAFU/025) |  | PSV/FF/PR/LAFU/025/F1 | 0.4 | 0.5 | 0.4 | 0.4 | 0.5 | 0.44
|  |  | PSV/FF/PR/LAFU/025/F2 | 0.4 | 0.4 | 0.4 | 0.5 | 0.4 | 0.42
|  |  | PSV/FF/PR/LAFU/025/F3 | 0.5 | 0.4 | 0.5 | 0.5 | 0.5 | 0.48
|  |  | PSV/FF/PR/LAFU/025/F4 | 0.5 | 0.5 | 0.4 | 0.4 | 0.5 | 0.46
|  |  | PSV/FF/PR/LAFU/025/F5 | 0.4 | 0.4 | 0.5 | 0.4 | 0.5 | 0.44
ACCEPTANCE CRITERIA : 0.45 m/s ± 20 % AS PER PROTOCOL No.PSV/PRO/001
ACCEPTANCE CRITERIA : 0.45 m/s ± 20 % AS PER EU GMP OR ISPE
TEST CARRIED OUT BY |  |  | TEST WITNESSED BY |  |  | TEST REVIEWED BY
For,Micron HVAC Pvt.Ltd. |  |  | For,Premium Serums and Vaccines Pvt. Ltd.